## Xe-133 submission instructions
When requesting to use Xe-133 please submit the following:
Specify the average and maximum activity (mCi) of Xenon-133 (Xe-133) to be used for any one study, and to be used in any one week.
Provide a diagram or the room where the Xe-133 will be used, showing all air supply, recirculation, inlet, and exhaust vents, with arrows to indicate the airflow patterns. If bulk xenon will be used, provide a diagram of the storage area, and describe the ventilation for that area.
Describe the method of exhausting air from the facility during times Xe-133 is used.
Describe the method used to prevent recirculation of the air to the rest of the facility during the times Xe-133 is used.
Specify air flow rates into and out of the room.
Specify how far the point of exhaust is from any unrestricted area or fresh air intake.
Describe the method used for administering the dose to the patient and the method used for trapping or exhausting the exhaled Xe-133.
Describe the procedure for testing the xenon trap (if used) to assure that it is properly trapping the xenon.
Provide emergency procedures in place to cope with large accidental releases of Xe-133, such as loss of an entire patient dose or spill of bulk quantity.
Demonstrate the exposure of facility personnel and the general public to Xe-133 is within limits of 25 TAC §289.202(ggg)(2).
Note: When performing calculations for room concentrations and room evacuation periods after an accidental release, you may use the Xe-133 Worksheet.
Indicate the frequency the associated ventilation systems will be tested to verify system integrity and effectiveness. Please note that any change(s) in use or exhaust air flow will affect all calculations.

## Xe-133 worksheet
XENON-133 WORK SHEET FILL OUT YELLOW CELLS ONLY Convenience document – not for official DSHS use | Disclaimer: Convenience document Not for official DSHS use
Preparer:
RAM License Number:
Date:
Facility:
Room number:
Xenon Concentration Formula & Evacuation Time Single Release
Activity per study [mCi, Xe-133]
N = Max number studies / week
Y = Activity per study [µCi] | 0
Activity per week [µCi] | 0
A = Maximum activity loss/week [µCi/wk] | 0
f = Estimated activity lost to the work areas per study (assume 20 %) | 0.2
R = Measured exhaust rate [cfm]
V = Room volume [cu ft]
C = Xenon Concentration [µCi/ml] | #DIV/0!
Regulatory limit [µCi/ml] | 0.0001
Evacuation time single release [min] | #DIV/0!
May this room be used for Xe-133? | #DIV/0!
YES = Adherence, NO = Response required | YES/NO
Negative pressure will be established, set, and checked annually
Established ventilation rates will be verified annually, as a minimum
Discharge Remote (> 25 ft) to all air intakes
Re-circulating air in the use room is prevented during use
Closed, self-shielded delivery system is used
Frequency and efficiency testing protocols of xenon/charcoal trap is consistent with manufacturer specifications (must maintain records)
Doors are closed and exhaust fans are on during, and for 30 minutes following the use of Xenon
RSO Signature

## Documentation
Documentation: |  | https://www.nrc.gov/docs/ML0827/ML082750413.pdf
Formulas:
A=N*Y*f
C=A/(R*1.699*10^6*40)
t=V/(-R*ln((V*2.832)/Y)